## AWG Specifications Table
AWG Specifications Table
Note: The information within this table is based on tertiary sources, original research, particular assumptions and calculations. Additionally, minor variations between data sources exist. This table should only be used as a general reference. No one is responsible for incorrect information found in this table. Use thereof is the sole responsibility of the user. Use at your own risk.
AWG sizes | Diameter (d) |  | Area |  | Copper resistance |  | Aluminum resistance |  | Maximum amps for |  | Turns of wire
| inches | mm | kcmil (d² x 1000 inches) | mm² | ohms per 1000 feet | ohms per km | ohms per 1000 feet | ohms per km | chassis wires | power trans-mission | per inch | per cm
0000 | 0.46 | 11.684 | 211.6 | 107.2193 | 0.04901 | 0.16079 | 0.0804 | 0.26378 | 380 | 302 | 2.17 | 0.856
000 | 0.4096 | 10.4038 | 167.7722 | 85.0114 | 0.0618 | 0.20276 | 0.101 | 0.33136 | 328 | 239 | 2.44 | 0.961
00 | 0.3648 | 9.2659 | 133.079 | 67.4321 | 0.07793 | 0.25568 | 0.128 | 0.41995 | 283 | 190 | 2.74 | 1.08
0 | 0.32486 | 8.2514 | 105.534 | 53.4749 | 0.09827 | 0.32241 | 0.161 | 0.52822 | 245 | 150 | 3.08 | 1.21
1 | 0.2893 | 7.3482 | 83.6945 | 42.4086 | 0.1239 | 0.4065 | 0.203 | 0.66601 | 211 | 119 | 3.46 | 1.36
2 | 0.25763 | 6.5438 | 66.3732 | 33.6318 | 0.1563 | 0.5128 | 0.256 | 0.8399 | 181 | 94 | 3.88 | 1.53
3 | 0.22942 | 5.8273 | 52.6335 | 26.6698 | 0.197 | 0.64633 | 0.323 | 1.0597 | 158 | 75 | 4.36 | 1.72
4 | 0.20431 | 5.1895 | 41.7426 | 21.1513 | 0.2485 | 0.81529 | 0.408 | 1.3386 | 135 | 60 | 4.89 | 1.93
5 | 0.18194 | 4.6213 | 33.1022 | 16.7731 | 0.3133 | 1.0279 | 0.514 | 1.6864 | 118 | 47 | 5.5 | 2.16
6 | 0.16202 | 4.1153 | 26.2505 | 13.3013 | 0.3951 | 1.2963 | 0.648 | 2.126 | 101 | 37 | 6.17 | 2.43
7 | 0.1443 | 3.6652 | 20.8225 | 10.5509 | 0.4982 | 1.6345 | 0.817 | 2.6804 | 89 | 30 | 6.93 | 2.73
8 | 0.1285 | 3.2638 | 16.5112 | 8.3664 | 0.6282 | 2.061 | 1.03 | 3.3793 | 73 | 24 | 7.78 | 3.06
9 | 0.1144 | 2.9058 | 13.0874 | 6.6315 | 0.7921 | 2.5988 | 1.3 | 4.2651 | 64 | 19 | 8.74 | 3.44
10 | 0.10189 | 2.588 | 10.3816 | 5.2604 | 0.9989 | 3.2772 | 1.64 | 5.3806 | 55 | 15 | 9.81 | 3.86
11 | 0.0907 | 2.3038 | 8.2265 | 4.1684 | 1.26 | 4.1339 | 2.07 | 6.7913 | 47 | 12 | 11 | 4.34
12 | 0.080808 | 2.0525 | 6.5299 | 3.3088 | 1.588 | 5.21 | 2.61 | 8.563 | 41 | 9.3 | 12.4 | 4.87
13 | 0.072 | 1.8288 | 5.184 | 2.6268 | 2.003 | 6.5715 | 3.29 | 10.794 | 35 | 7.4 | 13.9 | 5.47
14 | 0.064084 | 1.6277 | 4.1068 | 2.0809 | 2.525 | 8.2841 | 4.14 | 13.5827 | 32 | 5.9 | 15.6 | 6.14
15 | 0.0571 | 1.4503 | 3.2604 | 1.6521 | 3.184 | 10.4462 | 5.22 | 17.126 | 28 | 4.7 | 17.5 | 6.9
16 | 0.050821 | 1.2909 | 2.5828 | 1.3087 | 4.016 | 13.1759 | 6.59 | 21.6207 | 22 | 3.7 | 19.7 | 7.75
17 | 0.0453 | 1.1506 | 2.0521 | 1.0398 | 5.064 | 16.6142 | 8.31 | 27.2638 | 19 | 2.9 | 22.1 | 8.7
18 | 0.040303 | 1.0237 | 1.6243 | 0.82306 | 6.385 | 20.9482 | 10.5 | 34.4488 | 16 | 2.3 | 24.8 | 9.77
19 | 0.0359 | 0.91186 | 1.2888 | 0.65305 | 8.051 | 26.414 | 13.2 | 43.3071 | 14 | 1.8 | 27.9 | 11
20 | 0.031961 | 0.81181 | 1.0215 | 0.51761 | 10.15 | 33.3005 | 16.7 | 54.79 | 11 | 1.5 | 31.3 | 12.3
21 | 0.0285 | 0.7239 | 0.81225 | 0.41157 | 12.8 | 41.9948 | 21 | 68.8976 | 9 | 1.2 | 35.1 | 13.8
22 | 0.0253 | 0.64262 | 0.64009 | 0.32434 | 16.14 | 52.9528 | 26.5 | 86.9423 | 7 | 0.92 | 39.5 | 15.5
23 | 0.0226 | 0.57404 | 0.51076 | 0.25881 | 20.36 | 66.7979 | 33.4 | 109.5801 | 4.7 | 0.729 | 44.3 | 17.4
24 | 0.0201 | 0.51054 | 0.40401 | 0.20471 | 25.67 | 84.2192 | 42.1 | 138.1234 | 3.5 | 0.577 | 49.7 | 19.6
25 | 0.0179 | 0.45466 | 0.32041 | 0.16235 | 32.37 | 106.2008 | 53.1 | 174.2126 | 2.7 | 0.457 | 55.9 | 22
26 | 0.0159 | 0.40386 | 0.25281 | 0.1281 | 40.81 | 133.8911 | 67 | 219.8163 | 2.2 | 0.361 | 62.7 | 24.7
27 | 0.0142 | 0.36068 | 0.20164 | 0.10217 | 51.47 | 168.8648 | 84.4 | 276.9029 | 1.7 | 0.288 | 70.4 | 27.7
28 | 0.0126 | 0.32004 | 0.15876 | 0.080445 | 64.9 | 212.9265 | 106 | 347.769 | 1.4 | 0.226 | 79.1 | 31.1
29 | 0.0113 | 0.28702 | 0.12769 | 0.064701 | 81.84 | 268.5039 | 134 | 439.6325 | 1.2 | 0.182 | 88.8 | 35
30 | 0.01 | 0.254 | 0.1 | 0.050671 | 103.2 | 338.5827 | 169 | 554.4619 | 0.86 | 0.142 | 99.7 | 39.3
31 | 0.00893 | 0.22682 | 0.079745 | 0.040407 | 130.1 | 426.8373 | 213 | 698.8189 | 0.7 | 0.113 | 112 | 44.1
32 | 0.00795 | 0.20193 | 0.063203 | 0.032025 | 164.1 | 538.3858 | 269 | 882.5459 | 0.53 | 0.091 | 126 | 49.5
33 | 0.0071 | 0.18034 | 0.05041 | 0.025543 | 206.9 | 678.8058 | 339 | 1112.2047 | 0.43 | 0.072 | 159 | 62.4
34 | 0.0063 | 0.16002 | 0.03969 | 0.020111 | 260.9 | 855.9711 | 428 | 1404.1995 | 0.33 | 0.056 | 200 | 78.7
35 | 0.0056 | 0.14224 | 0.03136 | 0.01589 | 329 | 1079.3963 | 540 | 1771.6535 | 0.27 | 0.044 | 252 | 99.3
36 | 0.005 | 0.127 | 0.025 | 0.012668 | 414.8 | 1360.8924 | 681 | 2234.252 | 0.21 | 0.035 | 318 | 125
37 | 0.0045 | 0.1143 | 0.02025 | 0.010261 | 523.1 | 1716.2073 | 858 | 2814.9606 | 0.17 | 0.0289
38 | 0.004 | 0.1016 | 0.016 | 0.0081073 | 659.6 | 2164.042 | 1080 | 3543.3071 | 0.13 | 0.0228
39 | 0.0035 | 0.0889 | 0.01225 | 0.0062072 | 831.8 | 2729.0026 | 1360 | 4461.9423 | 0.11 | 0.0175
40 | 0.00314 | 0.079756 | 0.0098596 | 0.0049959 | 1049 | 3441.601 | 1720 | 5643.0446 | 0.09 | 0.0137
41 | 0.0028 | 0.07112 | 0.00784 | 0.0039726 | 1287.97 | 4225.6234
42 | 0.002494 | 0.063348 | 0.00622 | 0.0031517 | 1585.12 | 5200.5249
43 | 0.002221 | 0.056413 | 0.0049328 | 0.0024995 | 2070.36 | 6792.5197
44 | 0.001978 | 0.050241 | 0.0039125 | 0.0019825 | 2496.21 | 8189.6654
45 | 0.001761 | 0.044729 | 0.0031011 | 0.0015714 | 3206.24 | 10519.1601
46 | 0.001568 | 0.039827 | 0.0024586 | 0.0012458 | 4057.9 | 13313.3202
47 | 0.001397 | 0.035484 | 0.0019516 | 0.00098889 | 5009.75 | 16436.1877
48 | 0.001244 | 0.031598 | 0.0015475 | 0.00078415 | 6756.12 | 22165.748
49 | 0.001107 | 0.028118 | 0.0012254 | 0.00062094 | 8281.42 | 27170.0131
50 | 0.000986 | 0.025044 | 0.0009722 | 0.00049262 | 10388.22 | 34082.0866

## AWG Selection Guide
AWG selection guide Table
Note: The information within this table is conservative and is based on tertiary sources, original research, particular assumptions and calculations. Additionally, minor variations between data sources exist. This table should only be used as a general reference. No one is responsible for incorrect information found in this table. Use thereof is the sole responsibility of the user. Use at your own risk.
Circuit amps (A) |  | Circuit watts (W) |  | Length (feet)
@6V | @12V | @6V | @12V | 3 | 5 | 7 | 10 | 15 | 20 | 25
≤2.5 | ≤5 | ≤15 | ≤30 | 22 | 22 | 22 | 18 | 18 | 18 | 18 | Gage selection (AWG)
3 | 6 | 18 | 36 | 22 | 22 | 18 | 18 | 18 | 18 | 16
3.5 | 7 | 21 | 42 | 22 | 18 | 18 | 18 | 18 | 18 | 16
4 | 8 | 24 | 48 | 22 | 18 | 18 | 18 | 18 | 16 | 16
5 | 10 | 30 | 60 | 18 | 18 | 18 | 18 | 16 | 16 | 16
5.5 | 11 | 33 | 66 | 18 | 18 | 18 | 18 | 16 | 16 | 14
6 | 12 | 36 | 72 | 18 | 18 | 18 | 18 | 16 | 16 | 14
7.5 | 15 | 45 | 90 | 18 | 18 | 18 | 18 | 14 | 14 | 12
9 | 18 | 54 | 108 | 18 | 18 | 16 | 16 | 14 | 14 | 12
10 | 20 | 60 | 120 | 18 | 18 | 16 | 16 | 14 | 12 | 10
11 | 22 | 66 | 132 | 18 | 18 | 16 | 16 | 12 | 12 | 10
12 | 24 | 72 | 144 | 18 | 18 | 16 | 16 | 12 | 12 | 10
15 | 30 | 90 | 180 | 18 | 16 | 16 | 14 | 10 | 10 | 10
17.5 | 38 | 105 | 228 | 18 | 16 | 14 | 12 | 10 | 10 | 8
20 | 40 | 120 | 240 | 18 | 16 | 14 | 12 | 10 | 10 | 8
25 | 50 | 150 | 300 | 16 | 14 | 12 | 12 | 10 | 10 | 8
50 | 100 | 300 | 600 | 12 | 12 | 10 | 10 | 6 | 6 | 4
75 | 150 | 450 | 900 | 10 | 10 | 8 | 8 | 4 | 4 | 2
100 | 200 | 600 | 1200 | 10 | 8 | 8 | 6 | 4 | 4 | 2
Gage selection (AWG)